## Instructions
ASHRAE 62.1-2025 IAQP - Engineer Zone Input Workbook
Purpose | Separate input workbook for transferring zone data into the IAQP calculator.
Capacity | Each Zone Input sheet accepts 20 zones.
Input cells | Light-blue cells are engineer inputs. Gray project fields on the later Zone Inputs sheets are linked from the first sheet; keep their formulas intact.
Project fields | Enter project information once on Zone Inputs 1-20: Representative at A4, Engineer / Firm at E4, Contractor at J4 and Job at O4. To change it, edit those cells on the first sheet. Zone Inputs 21-40 and 41-60 update automatically.
Zone fields | Enter one project zone per blank row (rows 8-27) on the Zone Inputs sheets. No sample assumptions are prefilled.
Blank values | Blank optional inputs use the calculator defaults. Invalid numeric text and out-of-range values are import errors; correct them before calculating. Numeric zero remains an explicit override where allowed.
Outside air treatment | Select Yes in "Outside Air Treated with Carbon + Ionization" when the outdoor-air stream receives carbon plus ionization treatment. Leave blank or select No otherwise. Yes applies gas-phase carbon treatment to the outdoor air only, so a recirculating air handler can remain ionization only.
Product schedule | Optional columns Y:AA select the air purification schedule product per zone. Leave them blank to let the calculator suggest a device and quantity from the supply air. Device Quantity accepts a whole number; leave blank to auto-size.
Expansion | For more than 60 zones, copy a Zone Inputs sheet and give it a unique name beginning with Zone Inputs (for example, Zone Inputs 61-80). Keep row-7 headers and column positions. Clear the copied zone entries in A8:AA27 before entering additional zones; preserve the project-field links.
Examples | The Defaults & Examples sheet lists earlier starter selections for reference only. It is separate from the project-entry sheets and is not imported as zone data.
True defaults | The Value when blank column describes calculator fallback behavior, not a recommended project specification. Earlier starter examples can differ: blank filter inputs use None, not MERV 13 or MERV 8.
Project review | Enter the actual filters, air-cleaner selection, mounting location and design temperatures for your project. Earlier starter examples are not project data.
Field guide | See Field Guide for required and optional columns, units, blank-override behavior, PM2.5 efficiency format and system-type choices. Enter numeric values without unit text.
Profiles and test basis | See Profiles & Test Basis for all source-profile multipliers, emission/outdoor inputs, cleaner assumptions and missing product-test evidence. The selection label alone does not verify tested performance.
Numeric checks | Enter numbers without unit text. G and I require fractions from 0 to 1; E and N allow zero or positive numbers; AA requires a whole number of at least 1. Positive area, height, Ez and supply values are required when entered. Blank rows are skipped; partially filled rows are checked.

## Zone Inputs 1-20
ASHRAE 62.1-2025 IAQP Zone Inputs - Zones 1 to 20
Enter project information here once. The project fields on Zone Inputs 21-40 and 41-60 update automatically.
Representative's Name |  |  |  | Engineer's Name / Firm |  |  |  |  | Contractor's Name |  |  |  |  | Job Name
ZONE IDENTIFICATION |  |  |  |  | FILTRATION |  |  |  | IAQP SYSTEM | [7 empty] | COOLING DESIGN |  |  |  | HEATING DESIGN |  | OUTDOOR AIR TREATMENT | PRODUCT SCHEDULE (OPTIONAL)
Zone Name | Zone Use / Occupancy Category | Area (ft²) | Zone Height (ft) | Desired Occupant Quantity Override | Outside-Air Filter Efficiency | OA Filter PM2.5 Efficiency Override | Return-Air Filter Efficiency | Return Filter PM2.5 Efficiency Override | Zone Air Distribution Effectiveness Ez | System Type / Filter Location | Supply Air CFM Vpz | Design / Maximum Supply Air CFM Vpz,max | Desired OA CFM per Person | Source Profile | Air Cleaner Used (145.2 Tested) | Device Mounting Location | OA Design Dry Bulb (°F) | OA Design Wet Bulb (°F) | DOAS Cooling Coil LAT Dry Bulb (°F) | DOAS Cooling Coil LAT Wet Bulb (°F) | OA Heating Design Temperature (°F) | DOAS Heating LAT Dry Bulb (°F) | Outside Air Treated with Carbon + Ionization | Air Handler Type | Device Model | Device Quantity
Light-blue cells are engineer inputs; all project-entry rows start blank. See Defaults & Examples for calculator fallback values and earlier starter selections. Select Yes for outdoor-air treatment only when that stream is treated with carbon plus ionization.

## Zone Inputs 21-40
ASHRAE 62.1-2025 IAQP Zone Inputs - Zones 21 to 40
Project information is linked from Zone Inputs 1-20. Edit it there; keep the formulas in the gray fields below intact.
Representative's Name |  |  |  | Engineer's Name / Firm |  |  |  |  | Contractor's Name |  |  |  |  | Job Name
ZONE IDENTIFICATION |  |  |  |  | FILTRATION |  |  |  | IAQP SYSTEM | [7 empty] | COOLING DESIGN |  |  |  | HEATING DESIGN |  | OUTDOOR AIR TREATMENT | PRODUCT SCHEDULE (OPTIONAL)
Zone Name | Zone Use / Occupancy Category | Area (ft²) | Zone Height (ft) | Desired Occupant Quantity Override | Outside-Air Filter Efficiency | OA Filter PM2.5 Efficiency Override | Return-Air Filter Efficiency | Return Filter PM2.5 Efficiency Override | Zone Air Distribution Effectiveness Ez | System Type / Filter Location | Supply Air CFM Vpz | Design / Maximum Supply Air CFM Vpz,max | Desired OA CFM per Person | Source Profile | Air Cleaner Used (145.2 Tested) | Device Mounting Location | OA Design Dry Bulb (°F) | OA Design Wet Bulb (°F) | DOAS Cooling Coil LAT Dry Bulb (°F) | DOAS Cooling Coil LAT Wet Bulb (°F) | OA Heating Design Temperature (°F) | DOAS Heating LAT Dry Bulb (°F) | Outside Air Treated with Carbon + Ionization | Air Handler Type | Device Model | Device Quantity
Light-blue cells are engineer inputs; all project-entry rows start blank. See Defaults & Examples for calculator fallback values and earlier starter selections. Select Yes for outdoor-air treatment only when that stream is treated with carbon plus ionization.

## Zone Inputs 41-60
ASHRAE 62.1-2025 IAQP Zone Inputs - Zones 41 to 60
Project information is linked from Zone Inputs 1-20. Edit it there; keep the formulas in the gray fields below intact.
Representative's Name |  |  |  | Engineer's Name / Firm |  |  |  |  | Contractor's Name |  |  |  |  | Job Name
ZONE IDENTIFICATION |  |  |  |  | FILTRATION |  |  |  | IAQP SYSTEM | [7 empty] | COOLING DESIGN |  |  |  | HEATING DESIGN |  | OUTDOOR AIR TREATMENT | PRODUCT SCHEDULE (OPTIONAL)
Zone Name | Zone Use / Occupancy Category | Area (ft²) | Zone Height (ft) | Desired Occupant Quantity Override | Outside-Air Filter Efficiency | OA Filter PM2.5 Efficiency Override | Return-Air Filter Efficiency | Return Filter PM2.5 Efficiency Override | Zone Air Distribution Effectiveness Ez | System Type / Filter Location | Supply Air CFM Vpz | Design / Maximum Supply Air CFM Vpz,max | Desired OA CFM per Person | Source Profile | Air Cleaner Used (145.2 Tested) | Device Mounting Location | OA Design Dry Bulb (°F) | OA Design Wet Bulb (°F) | DOAS Cooling Coil LAT Dry Bulb (°F) | DOAS Cooling Coil LAT Wet Bulb (°F) | OA Heating Design Temperature (°F) | DOAS Heating LAT Dry Bulb (°F) | Outside Air Treated with Carbon + Ionization | Air Handler Type | Device Model | Device Quantity
Light-blue cells are engineer inputs; all project-entry rows start blank. See Defaults & Examples for calculator fallback values and earlier starter selections. Select Yes for outdoor-air treatment only when that stream is treated with carbon plus ionization.

## Lists
Filter Type | System Type | Device Mounting Location | Air Cleaner Used | Zone Use / Occupancy | Source Profile | Yes / No | Air Handler Type | Device Model
None | None - VAV / 100% OA | Inside air handler cabinet | Carbon Media and Ionization | Animal exam room (veterinary office) | Manual only | Yes | Air handler cabinet (small / closet) | AEIRO Pure Mini
MERV 8 | A - Constant volume | Duct mounted, downstream of the air handler | Ionization only | Animal imaging (MRI/CT/PET) | Low estimate (0.50x sample) | No | Rooftop or large built-up air handler | Phenomenal Aire Series C6 Pulse
MERV 11 | A - VAV / constant OA | Duct or plenum mounted at the air handler discharge |  | Animal operating rooms | Typical estimate (0.75x sample) |  | Duct or VAV downstream of the air handler | Phenomenal Aire Series C10 Pulse
MERV 13 | B - Constant volume | Cooling coil inlet |  | Animal postoperative recovery room | Classroom sample (1.00x) |  | Coil face (modular rail) | AEIRO Rail
MERV 14 | B - VAV / 100% OA | Inside ductless mini-split or fan coil housing |  | Animal preparation rooms | High estimate (1.50x sample) |  | Ductless mini-split or fan coil | Phenomenal Aire Series D18 Pulse
MERV 15 | B - VAV / constant OA | Floor standing in the occupied space |  | Animal procedure room |  |  | No ductwork (standalone room unit) | AEIRO Pure C150
MERV 16 |  |  |  | Animal surgery scrub
HEPA 99.97% |  |  |  | Large-animal holding room
Necropsy
Small-animal-cage room (static cages)
Small-animal-cage room (ventilated cages)
Booking/waiting
Cell
Dayroom
Guard stations
Art classroom
Assembly without fixed seats - concentrated (chairs only - fixed)
Classrooms (ages 5 to 8)
Classrooms (age 9+)
Corridors (ages 5+)
Daycare sickroom
Daycare (through age 4)
Information technology equipment facilities (occupiable) - Educational
Lecture hall (fixed seats)
Libraries - Educational
Media center
Multiuse assembly (tables and chairs)
Music/theater/dance
Science laboratories
University/college laboratories
Wood/metal shop
Bars, cocktail lounges
Cafeteria/fast-food dining
Kitchen (cooking)
Restaurant dining rooms
Break rooms
Coffee stations
Conference/meeting
Corridors - General
Occupiable storage rooms for liquids or gels
Barracks sleeping areas
Bedroom/living room
Laundry rooms, central
Laundry rooms within dwelling units
Lobbies/prefunction
Multipurpose assembly
Banks or bank lobbies
Bank vaults/safe deposit
Freezer and refrigerated spaces (<50 F [10 C])
Information technology equipment facilities (occupiable) - Misc.
Manufacturing where hazardous materials are not used
Manufacturing where hazardous materials are used
Pharmacy (prep. area)
Photo studios
Shipping/receiving
Sorting, packing, light assembly
Telephone closets
Transportation waiting
Warehouses
Main entry lobbies
Occupiable storage rooms for dry materials
Office space
Reception areas
Telephone/data entry
Auditorium seating area
Courtrooms
Legislative chambers
Libraries - Public Assembly
Lobbies
Museums (children's)
Museums/galleries
Places of religious worship
Common corridors - Residential
Sales (except as below)
Barbershop
Beauty and nail salons
Coin-operated laundries
Mall common areas
Pet shops (animal areas)
Supermarket
Bowling alley (seating)
Disco/dance floors
Gambling casinos
Game arcades
Gym, sports arena (play area)
Health club/aerobics room
Health club/weight rooms
Spectator areas
Stages, studios
Swimming (pool and deck)

## Defaults & Examples
Calculator Defaults & Earlier Starter Examples
REFERENCE ONLY — These rows are not imported as project zones.
Earlier starter examples are listed separately below. Enter actual project values in the blank Zone Inputs sheets.
Value when blank describes existing calculator fallback behavior. Confirm filters, cleaner selections and design temperatures for your project.
Input | Value when blank | Previous starter example
Zone height (ft) | 9 | Not prefilled
Outdoor-air filter | None | MERV 13
Return-air filter | None | MERV 8
Zone air distribution effectiveness (Ez) | 1 | 1
System type | B - Constant volume | B - Constant volume
Outdoor air per person (CFM/person) | 5 | Not prefilled
Source profile | Classroom sample (1.00x) | Classroom sample (1.00x)
Air cleaner | Carbon Media and Ionization (with an import warning) | Carbon Media and Ionization
Mounting location | No fallback; left blank | Inside air handler cabinet
Cooling outdoor-air dry bulb (°F) | 95 | 95
Cooling outdoor-air wet bulb (°F) | 76 | 76
Cooling leaving-air dry bulb (°F) | 55 | 55
Cooling leaving-air wet bulb (°F) | 55 | 55
Heating outdoor-air dry bulb (°F) | 20 | 20
Heating leaving-air dry bulb (°F) | 90 | 90
Outdoor air treated with carbon + ionization | No | Not prefilled
An earlier starter example remains an example even when it matches the calculator's fallback. No values from this reference sheet are copied into project rows.
Source: AEIRO Development import behavior and earlier starter values, reviewed 2026-10-08.

## Field Guide
Engineer Zone Input Workbook — Field Guide
Enter project zones only in rows 8–27 on the three Zone Inputs sheets. This guide is reference-only and is not imported as zone data.
Required means import validation needs the value. Optional means blank uses the behavior shown below; it does not mean the assumption is appropriate for every project.
Use numeric cells without unit text. Leave an optional override empty to use its default; numeric 0 is explicit where allowed. Invalid numeric text produces an import error that must be corrected.
OA = outdoor air; LAT = leaving-air temperature; CFM = cubic feet per minute; VAV = variable air volume. Confirm the actual filters, design conditions and system configuration.
Column | Input | Required / optional | Units and entry format | When blank
A | Zone Name | Recommended | Text; use a unique zone label. | The importer assigns Zone 1, Zone 2, etc. when a valid zone has no name.
B | Zone Use / Occupancy Category | Required | Choose a category from the dropdown. | An empty or unrecognized category is a validation error.
C | Area | Required | ft²; numeric value greater than 0. | Imports as 0 and fails validation.
D | Zone Height | Optional | ft; positive numeric value. | Uses 9 ft. Height is currently a reference input.
E | Desired Occupant Quantity Override | Optional override | Number of people, 0 or greater. A numeric 0 is an explicit override. | Uses area × the selected occupancy category's density / 1,000 ft².
F | Outside-Air Filter Efficiency | Optional selection | Choose a filter rating from the dropdown. | Uses None (0 PM2.5 filter efficiency), unless G supplies an override.
G | OA Filter PM2.5 Efficiency Override | Optional override | Fraction from 0 to 1; enter 0.85 for 85%. See the PM2.5 format note below. | Uses the PM2.5 efficiency associated with the filter selected in F.
H | Return-Air Filter Efficiency | Optional selection | Choose a filter rating from the dropdown. | Uses None (0 PM2.5 filter efficiency), unless I supplies an override.
I | Return Filter PM2.5 Efficiency Override | Optional override | Fraction from 0 to 1; enter 0.85 for 85%. See the PM2.5 format note below. | Uses the PM2.5 efficiency associated with the filter selected in H.
J | Zone Air Distribution Effectiveness Ez | Optional | Unitless number greater than 0; normally 0.5–1.2. Enter the project value. | Uses 1.
K | System Type / Filter Location | Optional; confirm | Select the actual system. The six dropdown choices are explained below. | Uses B - Constant volume. Unrecognized text also falls back to that choice, with a warning.
L | Supply Air CFM Vpz | Required | CFM, greater than 0. Constant volume: design supply. VAV: minimum supply (Vpz,min). | Imports as 0 and fails validation.
M | Design / Maximum Supply Air CFM Vpz,max | Required for VAV | CFM. For VAV, must exceed L. For constant volume, optional; if entered, must be at least L. | VAV: validation error. Constant volume: L remains the design supply; no VAV airflow reduction is applied.
N | Desired OA CFM per Person | Optional | CFM/person; numeric value, 0 or greater. Zone desired OA = this value × occupant count. | Uses 5 CFM/person. A numeric 0 remains an explicit zero.
O | Source Profile | Optional selection | Choose the applicable profile from the dropdown; confirm the project assumption. | Uses Classroom sample (1.00x).
P | Air Cleaner Used (145.2 Tested) | Optional; confirm | Dropdown: Carbon Media and Ionization, or Ionization only. | Uses Carbon Media and Ionization and issues an import warning. Unsupported text is a validation error.
Q | Device Mounting Location | Optional selection | Choose the intended mounting location from the dropdown. | No mounting override is imported. The product schedule uses the selected device's default mounting.
R | OA Design Dry Bulb | Optional | °F; cooling outdoor-air dry-bulb temperature. | Uses 95°F.
S | OA Design Wet Bulb | Optional | °F; cooling outdoor-air wet bulb. Must not exceed R. | Uses 76°F; still checked against R.
T | DOAS Cooling Coil LAT Dry Bulb | Optional | °F; cooling leaving-air dry bulb (LAT). | Uses 55°F.
U | DOAS Cooling Coil LAT Wet Bulb | Optional | °F; cooling leaving-air wet bulb. Must not exceed T. | Uses 55°F; still checked against T.
V | OA Heating Design Temperature | Optional | °F; heating outdoor-air dry bulb. | Uses 20°F.
W | DOAS Heating LAT Dry Bulb | Optional | °F; heating leaving-air dry bulb. | Uses 90°F.
X | Outside Air Treated with Carbon + Ionization | Optional selection | Yes / No dropdown. Select Yes only when that treatment is applied to the outdoor-air stream. | Uses No. This flag does not add carbon treatment to a recirculated stream selected as Ionization only.
Y | Air Handler Type | Optional schedule | Choose the air-handler category from the dropdown. | No category override; the schedule suggests a device using its default selection logic and supply airflow.
Z | Device Model | Optional override | Select an available model from the dropdown. | The schedule suggests a model from the air-handler type and supply airflow.
AA | Device Quantity | Optional override | Whole number, 1 or greater, for a fixed device count. | The schedule sizes quantity from device capacity and supply airflow, or requests coordination for models not sized by CFM.
PM2.5 overrides — columns G and I
Use a decimal fraction from 0 to 1: 0 = 0%, 0.85 = 85%, and 1 = 100%. Enter 0.85, not the whole number 85. The importer does not divide whole-number percentages by 100.
A true numeric Excel percentage such as 85% stores 0.85 and imports correctly. A text string such as '85%' is rejected as nonnumeric. Prefer entering 0.85 directly.
A blank G uses the filter rating in F; a blank I uses H. An explicit numeric 0 overrides the selected filter with zero filter efficiency. Air-cleaner particulate treatment is applied separately.
G and I are checked as fractions from 0 to 1 in the workbook and importer. Invalid pasted values are reported during import even if spreadsheet validation was bypassed. Correct errors before calculating.
System-type choices — column K
Select the actual dropdown label. A and B describe the calculator's cleaner-location branches, not equipment brands. The descriptions below concern branch treatment; separate filter and cleaner selections still apply.
Dropdown choice |  | Calculator branch |  | Airflow entries
None - VAV / 100% OA |  | 100% outdoor-air VAV branch without cleaner credit in the branch equation. |  | L = minimum CFM; M = maximum CFM, strictly greater than L.
A - Constant volume |  | Constant-volume branch; cleaner credit applies to the recirculated stream. |  | L = design CFM; M is optional.
A - VAV / constant OA |  | VAV with constant outdoor airflow; cleaner credit applies to the recirculated stream. |  | L = minimum CFM; M = maximum CFM, strictly greater than L.
B - Constant volume |  | Constant-volume branch; cleaner credit also applies to the outdoor-air stream. |  | L = design CFM; M is optional. This is the blank-input fallback.
B - VAV / 100% OA |  | 100% outdoor-air VAV branch with cleaner credit on the outdoor-air stream. |  | L = minimum CFM; M = maximum CFM, strictly greater than L.
B - VAV / constant OA |  | VAV with constant outdoor airflow; cleaner credit also applies to the outdoor-air stream. |  | L = minimum CFM; M = maximum CFM, strictly greater than L.
All choices containing VAV require both L and M, with M greater than L. The calculator derives its VAV airflow fraction from L ÷ M. Constant-volume branches use a fraction of 1.
Project fields and final checks
Enter project information once on Zone Inputs 1-20: Representative A4, Engineer / Firm E4, Contractor J4 and Job O4. These text fields are optional for parsing; blanks stay blank. The gray fields on later sheets link here automatically. Edit the first sheet and keep the linked formulas intact.
Choose a recognized occupancy category and enter positive area and supply airflow. Cooling wet bulb must not exceed dry bulb (S ≤ R and U ≤ T). Desired outdoor airflow (N × occupants) must stay below L under the current validator.
Keep column positions and row-7 headers intact. Completely blank rows are skipped; partially filled rows are validated. For more than 60 zones, copy a sheet, keep its name beginning with Zone Inputs, and clear copied zone entries before entering new zones. Review all import errors and warnings.
See Defaults & Examples for blank-input fallbacks. Profiles & Test Basis documents source assumptions, cleaner coefficients and the product-test evidence still needed.
Source: AEIRO Development workbook importer, validation, system mapping and schedule behavior; reviewed 2026-10-08.

## Profiles & Test Basis
Zone Input — Profiles & Test Basis
Evidence status: model inputs are documented. Applicable model/configuration-specific laboratory reports have not been verified in the reviewed materials.
This sheet is reference-only and is ignored by the zone importer. Confirm project assumptions and applicable performance evidence before relying on a calculated result.
Source profiles — column O
Dropdown choice | Multiplier | What the current calculator assumes
Manual only | 0 | Sets every modeled indoor emission to zero. This workbook has no custom-emission input columns; selecting Manual only does not import project-specific emission overrides.
Low estimate (0.50x sample) | 0.5 | Uses 50% of every classroom sample emission rate. An AEIRO scenario multiplier, not a separately measured low-source dataset.
Typical estimate (0.75x sample) | 0.75 | Uses 75% of every classroom sample emission rate. An AEIRO scenario multiplier, not a universal typical-building dataset.
Classroom sample (1.00x) | 1 | Uses the unscaled classroom sample emission rates below. This is also the blank-profile fallback.
High estimate (1.50x sample) | 1.5 | Uses 150% of every classroom sample emission rate. An AEIRO scenario multiplier, not a separately measured high-source dataset.
Emission used = base emission × profile multiplier, in µg/(h·m²). Total zone emission = emission used × area in ft² × 0.092903, in µg/h.
Profiles scale indoor emissions only. They do not change outdoor concentrations, gas-removal coefficients or PM2.5 cleaner rules. Unrecognized profile text currently falls back to a multiplier of 1; use the dropdown.
Sample provenance: the indoor and outdoor values below match Table 3 of Trane IAQ-WPR001B-EN (May 2026). The example concerns classrooms, ages 5–8. It attributes emissions to the ASHRAE classroom calculator and outdoor values to the 62.1-2019 User’s Manual.
These example values are not a site survey or a validated profile for every occupancy. Low / Typical / High scale the same data; changing the occupancy category does not select a different emission dataset.
Manual only is a zero-indoor-source scenario in this workflow. A project requiring custom emission rates needs a supported, reviewed input method; the profile name alone does not provide one.
Compound inputs currently used by the model
B and C are the classroom sample inputs. D contains inherited AEIRO gas-removal assumptions for the combined cleaner selection, not verified product ratings. Trane’s separate cleaner example is not the source of D.
Compound | Base emission µg/(h·m²) | Outdoor µg/m³ | Gas-removal assumption | Qualification
Acetaldehyde | 16.5 | 1.77 | 8.8% | Model coefficient; applicable product test report not verified.
Acetone | 37.7 | 5.7 | 9.6% | Model coefficient; applicable product test report not verified.
Benzene | 0.21 | 3.83 | 5.3% | Model coefficient; applicable product test report not verified.
Dichloromethane | 1.18 | 0 | 16% | Model coefficient; applicable product test report not verified.
Formaldehyde | 59.2 | 3.71 | 9.3% | Model coefficient; applicable product test report not verified.
Naphthalene | 0.38 | 2.1 | 7.4% | Model coefficient; applicable product test report not verified.
Phenol | 6.25 | 2.31 | 7.2% | Model coefficient; applicable product test report not verified.
Tetrachloroethylene | 0.14 | 4.07 | 18.8% | Model coefficient; applicable product test report not verified.
Toluene | 3.84 | 4.15 | 5.1% | Model coefficient; applicable product test report not verified.
Xylene, total | 3.13 | 2.61 | 6.3% | Model coefficient; applicable product test report not verified.
Carbon monoxide | 0 | 1.12 | 0% | Model coefficient; applicable product test report not verified.
PM2.5 | 0 | 5.7 | Dynamic | PM2.5 uses the separate rule below; it is not a gas-phase 145.2 rating.
Ozone | 0 | 2.36 | 9.6% | Model coefficient; applicable product test report not verified.
Ammonia | 0 | 0 | 11.5% | Model coefficient; applicable product test report not verified.
Base indoor emissions for carbon monoxide, PM2.5, ozone and ammonia are zero in this sample and remain zero under every multiplier. A sample zero does not establish that a real project has no such source.
Cleaner selections and outdoor-air treatment — columns P and X
Selection / condition | Gas / VOC credit |  | PM2.5 and application
Carbon Media and Ionization | Uses the inherited per-compound coefficients in D above. |  | PM2.5 = max(80%, return-filter efficiency). The selected system branch determines where cleaner credit applies; see Field Guide.
Ionization only | No gas / VOC cleaner credit in the recirculated stream. |  | Same PM2.5 max rule. Ionization selection alone does not provide gas-removal credit.
X = Yes with Ionization only | Applies separate carbon treatment to outdoor gas concentrations; it does not add recirculated gas credit. |  | Starts with inherited gas coefficients when no OA efficiency is entered. The solver may report a required OA efficiency and a conditional result; that requirement is not measured performance.
The 80% minimum particulate credit is an inherited client specification in the engine; an applicable test report was not found. With return MERV 8 (model lookup 20%), the cleaner credit is 80%; with MERV 13 (85%), it is 85%. The efficiencies are not added or combined in series.
An explicit return-filter override of 0 still leaves the 80% ionization minimum. OA filtration separately reduces incoming PM2.5. Selecting combined carbon and ionization prevents X from adding another carbon-treatment credit.
Device model, quantity and mounting choices describe the equipment schedule; they do not select different gas coefficients or a different 80% assumption. The “145.2 Tested” dropdown label is not itself evidence that the selected device/configuration has been tested.
Test basis and evidence needed to close the item
Traceable: all five profile multipliers, 14 base emission/outdoor entries, inherited gas coefficients and cleaner-selection rules match the current Development model. The classroom reference supports example source inputs, not the selected product’s removal performance.
Not verified: model/media/configuration-specific gas-phase reports supporting the inherited coefficients, and particulate reports supporting the 80% ionization minimum. No report identifiers or applicable test conditions were available in the reviewed project materials.
ASHRAE Standard 145.2-2025 covers full-scale in-duct gas-phase air-cleaning device tests under steady-state, elevated challenge conditions. Its scope supports device comparisons; it does not directly predict a particular application and does not establish a PM2.5 efficiency.
For review, supply the report ID, laboratory, date and method/edition; tested device, media and configuration; airflow and relevant environmental/challenge conditions; measured per-contaminant results; and any duration, aging or end-of-useful-life basis. Relate each credited value to that configuration.
For ionization / PM2.5, supply applicable particulate-performance evidence and its operating conditions. A gas-phase 145.2 reference alone cannot substantiate the model’s 80% particulate assumption.
If an outdoor-air result is conditional on a required carbon efficiency, verify that the specified equipment can meet that requirement under the project conditions. A solver requirement is a design target, not a laboratory result.
PL-083 documentation is implemented; product-test evidence remains open. These notes preserve and explain the present calculation assumptions rather than certifying their applicability to a specific installation.
Sources and review record
[1] AEIRO Development model: src/lib/iaqp/data/compounds.ts, data/lists.ts and engine.ts; reviewed at commit 5cbe274f852fbe84c452ce2d66f9bfd630a6538d on 2026-10-08.
[2] Trane, Compliance with the Indoor Air Quality Procedure of ASHRAE Standard 62.1 — IAQP Updates and Examples; IAQ-WPR001B-EN, May 2026; example context p. 6 and Table 3 p. 7.
https://elibrary.tranetechnologies.com/public/commercial-hvac/Literature/White%20Paper/IAQ-WPR001B-EN_05112026.pdf
[3] ASHRAE, Titles, Purposes and Scopes: Standard 145.2-2025. Method scope only; no specific AEIRO product report is established by this reference.
https://www.ashrae.org/technical-resources/standards-and-guidelines/titles-purposes-and-scopes